## Design PUE
EDGE V3 Buildings Design PUE Reporting for Data Centers (v 0.1)
Subproject Name
Project No.
File No.
Design Annualized Mechanical Load Component (Annualized MLC)
| data center design ITE load at 100% (kW) | 5000 | USER INPUT
| calculated mechanical energy at 25% of the design ITE load (kWh/year) | 7000000 | USER INPUT
| calculated mechanical energy at 50% of the design ITE load (kWh/year) | 8000000 | USER INPUT
| calculated mechanical energy at 75% of the design ITE load (kWh/year) | 9000000 | USER INPUT
| calculated mechanical energy at 100% of the design ITE load (kWh/year) | 10000000 | USER INPUT
| Design annualized MLC | 0.3105
Design ELC (Electrical Losses)
| Design ELC 100%, unitless* | 0.11 | USER INPUT
| Design ELC 75%, unitless* | 0.098 | USER INPUT
| Design ELC 50%, unitless* | 0.094 | USER INPUT
| Design ELC 25%, unitless* | 0.093 | USER INPUT
*Leave default values unless calculations are provided as part of the submission
| Average Mechanical energy (kWh) | 8500000
| Average Efficiency losses (kWh) | 4325250
| Other energy uses required for the functioning of the data center - E.g. Lighting (kWh) | 1000 | USER INPUT
| On-site renewable (up to 10%) (kWh) | 0
| Data center proceses - Mechanical energy + Efficiency losses + Other energy uses (kWh) | 12826250
| ITE energy - assumed an average 62.5% load (kWh) | 27375000
| EDGE design PUE proxy (dimentionless) | 1.4685

## Definitions
Abb. |  | Definition | Notes
MLC | Mechanical Load Component | A measure of the energy required by the data center’s mechanical systems relative to the IT load. It accounts for process cooling, process ventilation, and process heating. The Annualized MLC is calculated across 25%, 50%, 75%, and 100% ITE design-load conditions. | MLC can be calculated with dynamic simulation software like Energy Plus
ELC | Electrical Loss Component | A measure of the electrical losses incurred in delivering power to the IT equipment. It combines losses from the UPS segment and ITE distribution segment and is calculated separately at 25%, 50%, 75%, and 100% of ITE design load. The actual IT equipment is not part of the distribution segment. The ASHRAE/ANSI Standard 90.4-2025 provides detailed examples and charts in Informative Appendix C to guide users through the step-by-step calculation of ELC, including various UPS redundancy configurations | At each of the 25%, 50%, 75%, and 100% ITE design-load points: Calculate the UPS segment loss using the UPS efficiency at that load. Calculate the ITE distribution segment loss, including applicable transformers, feeders, PDUs, switchgear and branch circuits between the UPS output and ITE connection point. Add the two loss components: ELC = UPS segment loss + ITE distribution segment loss Note: This cannot be done in dynamic simulation software like EnergyPlus
PUE | Power Usage Effectiveness | PUE measures the overall energy efficiency of a data center by comparing its total annual energy use with the energy consumed by the IT equipment (ITE) | The calculation output is a proxy design PUE valid for EDGE reporting purposes but does not substitute a PUE calculated through direct measurement.
Reference: ASHRAE 90.4-2025